## Equations
Equations | Givens
| Inflow Infiltration Rate = | 750 | gal/ac/day
| One (1) day = | 1440 | min
| # persons per LUE | 3.5 | People/LUE
| 1 Household (LUE) per day | 0.0024306 | Person/LUE/min
| Average # gallons/person/day | 80 | gal/person/day | 0.055556 | gal/person/min
| 1 square foot | 2.2957e-05 | acre
| 1 acre | 43560 | SF
| 1 gal | 0.13368 | ft cubed
5.6458
142.8458
𝑃𝑖𝑝𝑒 𝐴𝑟𝑒𝑎=𝜋𝑟^2
𝑊𝑒𝑡 𝑃𝑒𝑟𝑖𝑚𝑒𝑡𝑒𝑟=𝜋∗𝑑/12
𝐻𝑦𝑑𝑟𝑎𝑢𝑙𝑖𝑐 𝑅𝑎𝑑𝑖𝑢𝑠=(𝑃𝑖𝑝𝑒 𝐴𝑟𝑒𝑎)/(𝑊𝑒𝑡 𝑃𝑒𝑟𝑖𝑚𝑒𝑡𝑒𝑟)
𝐹𝑢𝑙𝑙 𝐹𝑙𝑜𝑤=(𝑃𝑖𝑝𝑒 𝐴𝑟𝑒𝑎∗𝑉𝑒𝑙𝑜𝑐𝑖𝑡𝑦 ∗60 𝑆𝑒𝑐𝑜𝑛𝑑𝑠)/(0.133681 𝑓𝑡^3 )
* (# of LUEs) *
𝐴𝑣𝑒𝑟𝑎𝑔𝑒 𝐷𝑟𝑦 𝑊𝑒𝑎𝑡ℎ𝑒𝑟 𝐹𝑙𝑜𝑤=((80 𝑔𝑎𝑙)/(𝑝𝑒𝑟𝑠𝑜𝑛−𝑑𝑎𝑦) * (# of LUEs) * (3.5 𝑃𝑒𝑜𝑝𝑙𝑒)/(24 ℎ𝑜𝑢𝑟𝑠 ∗60 𝑀𝑖𝑛𝑢𝑡𝑒𝑠)
𝑃𝑒𝑎𝑘 𝐷𝑟𝑦 𝑊𝑒𝑎𝑡ℎ𝑒𝑟 𝐹𝑙𝑜𝑤=(18 + (0.018∗𝐴𝐷𝑊𝐹)^0.5)/(4+(0.018 ∗𝐴𝐷𝑊𝐹)^0.5 )∗𝐴𝐷𝑊𝐹
𝐼𝑛𝑓𝑙𝑜𝑤 & 𝐼𝑛𝑓𝑖𝑙𝑡𝑟𝑎𝑡𝑖𝑜𝑛=((750 𝑔𝑎𝑙/(𝑎𝑐𝑟𝑒−𝑑𝑎𝑦) ∗ 𝐴𝑟𝑒𝑎))/((24 𝐻𝑜𝑢𝑟𝑠 ∗60 𝑀𝑖𝑛𝑢𝑡𝑒𝑠) )
𝑉𝑒𝑙𝑜𝑐𝑖𝑡𝑦=(1.49/0.013)∗𝐻𝑦𝑑𝑟𝑎𝑢𝑙𝑖𝑐 𝑅𝑎𝑑𝑖𝑢𝑠^0.67 ∗% 𝑠𝑙𝑜𝑝𝑒^0.5
𝐹𝑢𝑙𝑙 𝐹𝑙𝑜𝑤=(𝑃𝑖𝑝𝑒 𝐴𝑟𝑒𝑎 ∗𝑉𝑒𝑙𝑜𝑐𝑖𝑡𝑦 ∗60 𝑠𝑒𝑐𝑜𝑛𝑑𝑠)/(0.133681 𝑓𝑡^3 )
𝑃𝑒𝑎𝑘 𝑊𝑒𝑡 𝑊𝑒𝑎𝑡ℎ𝑒𝑟 𝐹𝑙𝑜𝑤=𝑃𝑒𝑎𝑘 𝐷𝑟𝑦 𝑊𝑒𝑎𝑡ℎ𝑒𝑟 𝐹𝑙𝑜𝑤+𝐼𝑛𝑓𝑙𝑜𝑤 & 𝐼𝑛𝑓𝑖𝑙𝑡𝑟𝑎𝑡𝑖𝑜𝑛

## LUE
Area | Property | Property Size (ac) | Land Use | Size | LUE Conversion Factor | Total # of LUEs per Property | Total LUEs | Total Acres
A | A1 | 16.8834 | Church | 500 Seats | 1 LUE per 70 Seats | 7.1429 | 159.0125 | 78.5354
B | B1 | 7.673 | School | 80 Students | 1 LUE per 13 Students | 6.1538
| B2 | 4.57 | Church | 560 Seats | 1 LUE per 70 Seats | 8
| B3 | 6.048 | Apartments | 300 Units | 0.5 LUEs per Unit | 110
C | C1 | 5.812 | Office | 30,000 sqft | 1 LUE per 3000 sqft | 10
| C2 | 9.675 | Warehouse | 24,560 sqft | 1 LUE per 4000 sqft | 6.14
D | D1 | 11.4817 | Warehouse | 11,530 sqft | 1 LUE per 4000 sqft | 2.8825
| D2 | 2.045 | Office | 8,110 sqft | 1 LUE per 3000 sqft | 2.7033
| D3 | 3.5656 | Office | 6,770 sqft | 1 LUE per 3000 sqft | 2.2567
E | E1 | 7.7941 | Warehouse | 10,400 sqft | 1 LUE per 4000 sqft | 2.6
| E2 | 2.9875 | Office | 3,400 sqft | 1 LUE pe 3000 sqft | 1.1333

## Capacity
Pipe # | Upstream Manhole UID | Downstream Manhole UID | Pipe Size (in) | Pipe Length (ft) | Pipe Area (ft^2) | Wet Perimeter (ft) | Hydraulic Radius (ft) | Pipe Slope (%) | Pipe Slope Source | Contributing Areas | Total Area (AC) | Total LUEs | ADWF (gpm) | PDWF (gpm) | I&I (gpm) | PWWF (gpm) | Velocity (ft/s) | Full Flow (gpm) | 65% Full Flow (gpm) | Is PDWF Acceptable (65% full flow) or Exceeding? | 85% Full Flow* (gpm) | Is PWWF Acceptable (85% full flow) or Exceeding?
1466745 | m1 (1433857) | m2 (1433812) | 8 | 300 | 0.34907 | 2.0944 | 0.16667 | 0.76% | Survey | A1,B3,B2,C1 | 5.12 | 135.1429 | 26.2778 | 104.7566 | 2.6667 | 107.4232 | 3.0081 | 471.2781 | 306.3308 | Acceptable | 400.5864 | Acceptable
1466743 | m2 (1433812) | m3 (1433813) | 8 | 300 | 0.34907 | 2.0944 | 0.16667 | 0.36% | Asbuilt | A,B,C | 50.6614 | 147.4367 | 28.6682 | 113.7309 | 26.3861 | 140.117 | 2.0703 | 324.3559 | 210.8313 | Acceptable | 275.7025 | Acceptable
1466734 | m3(1433813) | m4 (1433850) | 8 | 281.93 | 0.34907 | 2.0944 | 0.16667 | 2% | Asbuilt | A,B,C | 50.6614 | 147.4367 | 28.6682 | 113.7309 | 26.3861 | 140.117 | 4.8797 | 764.5141 | 496.9342 | Acceptable | 649.837 | Acceptable
1466733 | m4 (1433850) | m5 (1433851) | 8 | 300 | 0.34907 | 2.0944 | 0.16667 | 0.4% | Asbuilt | A,B,C | 50.6614 | 147.4367 | 28.6682 | 113.7309 | 26.3861 | 140.117 | 2.1823 | 341.9011 | 222.2357 | Acceptable | 290.6159 | Acceptable
1466732 | m5 (1433851) | m6 (1433852) | 8 | 261.51 | 0.34907 | 2.0944 | 0.16667 | 0.481% | Asbuilt | A,B,C,E2 | 53.6489 | 148.57 | 28.8886 | 114.5551 | 27.9422 | 142.4973 | 2.393 | 374.9092 | 243.691 | Acceptable | 318.6728 | Acceptable
1466731 | m6 (1433852) | m7 (1433853) | 8 | 149.49 | 0.34907 | 2.0944 | 0.16667 | 0.4075% | Asbuilt | A,B,C,D,E2 | 70.7413 | 156.4125 | 30.4135 | 120.2446 | 36.8444 | 157.089 | 2.2027 | 345.1068 | 224.3194 | Acceptable | 293.3408 | Acceptable
1466730 | m7 (1433853) | m8 (1433857) | 8 | 226.01 | 0.34907 | 2.0944 | 0.16667 | 1.191% | Asbuilt | A,B,C,D,E | 78.5354 | 159.0125 | 30.9191 | 122.1255 | 40.9038 | 163.0294 | 3.765 | 589.8614 | 383.4099 | Acceptable | 501.3822 | Acceptable
1466729 | m8 (1433857) | m9 (1433855) | 8 | 321.06 | 0.34907 | 2.0944 | 0.16667 | 1.78% | Asbuilt | A,B,C,D,E | 78.5354 | 159.0125 | 30.9191 | 122.1255 | 40.9038 | 163.0294 | 4.6035 | 721.2412 | 468.8068 | Acceptable | 613.055 | Acceptable
1466728 | m9 (1433855) | m10 (1433856) | 8 | 300 | 0.34907 | 2.0944 | 0.16667 | 3.347% | Asbuilt | A,B,C,D,E | 78.5354 | 159.0125 | 30.9191 | 122.1255 | 40.9038 | 163.0294 | 6.3129 | 989.0443 | 642.8788 | Acceptable | 840.6876 | Acceptable
1466700 | m10 (1433856) | m11 (1432085) | 8 | 403.65 | 0.34907 | 2.0944 | 0.16667 | 0.4% | Asbuilt | A,B,C,D,E | 78.5354 | 159.0125 | 30.9191 | 122.1255 | 40.9038 | 163.0294 | 2.1823 | 341.9011 | 222.2357 | Acceptable | 290.6159 | Acceptable
1471500 | m11 (1432085) | m12 (1436930) | 36 | 502.32 | 7.0686 | 9.4248 | 0.75 | 20% | Asbuilt | A,B,C,D,E | 78.5354 | 159.0125 | 30.9191 | 122.1255 | 40.9038 | 163.0294 | 42.2716 | 134110.5415 | 87171.852 | Acceptable | 107288.4332 | Acceptable
* For sewer mains eighteen (18) inches in diameter or larger, the main shall be designed such that the PWWF shall not exceed eighty (80) percent of the capacity of the pipe flowing full. Full flow shall mean the capacity of a pipe that has a depth of flow equal to the pipe diameter, and the hydraulic grade is at the inside top of the pipe.